PRODUCT BULLETIN

MODEL HJ  MULTISTAGE HSC

The American-Marsh Model HJ multistage splitcase pumps are designed for long, dependable life in many applications.  The Model HJ multistage splitcase pumps operate at 1750 RPM quietly and efficiently.  The HJ product line, with its many options, allows the end user increased flexibility in todays pump applications.

Material Specifications

| PART | CONSTRUCTION |
| --- | --- |
|  | BRONZE FITTED | ALL IRON | NI-RESIST FITTED | 316SS FITTED |
| Casing | Cast Iron | Cast Iron | Cast Iron | Cast Iron |
| Impellers | Bronze | Cast Iron | Ni-Resist | 316 Stainless Steel |
| Stuffing Boxes | Cast Iron | Cast Iron | Cast Iron | Cast Iron |
| Shaft | 420 Stainless Steel | 420 Stainless Steel | 316 Stainless Steel | 316 Stainless Steel |
| Lantern Rings | Bronze | Cast Iron | Ni-Resist | 316 Stainless Steel |
| Stuffing Box Glands | Bronze | Cast Iron | Ni-Resist | 316 Stainless Steel |
| Shaft Sleeves | Bronze | 416 Stainless Steel | 316 Stainless Steel | 316 Stainless Steel |
| Bearing Housings | Cast Iron | Cast Iron | Cast Iron | Cast Iron |
| Mechanical Seal | Carbon/Si-C/Buna | Carbon/Si-C/Buna | Carbon/Si-C/Buna | Carbon/Si-C/Buna |

MODEL HJ SPECIFICATIONS

Casing:  The casing is of high tensile cast iron or other specified material.  It is of the volute type, split on the horizontal center line with the suction and discharge flanges casted integral with the lower half.   The casing utilizes Thru-Bore lineboring technology simplifying the machining operation and allows the advantage of using only a few modular rotating assemblies.  The Thru-Bore feature allows for the complete removal and replacement of the stuffing boxes without replacing the casing.  Removal of the upper half of the casing gives complete access to the interior of the pump without disturbing the piping connections or pump alignment.

Impellers:  The impellers are of the single suction, enclosed, non-overloading type.  They are placed back to back to balance the end thrust without the use of extra seal rings or other balancing devices.   Impellers are made of bronze, or other special material, machined and polished all over, and dynamically and hydraulically balanced.  They are keyed to the shaft, secured by lock nuts and adjustable for position.

Case Wear Rings:  Case wear rings are made of bronze or other specified material.  They are designed with a large wearing surface with the diameter at wearing surface reduced to a minimum, and are firmly secured to the casing by dowel pins.

Shaft:  The shaft is of stainless steel, ground to accurate dimensions and polished to a smooth surface.  It is designed for extra stiffness to avoid all critical speeds in operation, and is threaded for bearing and lock nuts.

Stuffing Boxes:  The stuffing boxes are extra deep, designed for packing or mechanical seals.  The stuffing boxes are completely removable and replaceable.

Glands:  The glands are of the hinge bolt type, split for easy removal and fastened together with capscrews.

Bearings:  Both the inboard and outboard ball bearings are of the single row, deep groove type, precision grade, with cartridge mounting, permitting the removal of the shaft without exposing or disturbing the bearing assembly.  They are of extra large capacity for both radial and thrust loads, and are locked to the shaft with nut and positive nut lock.  The outboard bearing is confined rigidly in the bearing housing to take the end thrust, while the inboard bearing is set with sufficient clearance to allow for shaft expansion.  Each bearing is designed for grease lubrication and is provided with a water slinger to prevent leakage from the stuffing box into the bearing.  A grease zerk fitting is furnished for each bearing.

HJ Sectional Drawing

| Item Number | Item Description | Num. Req. |  | Item Number | Item Description | Num. Req. |
| --- | --- | --- | --- | --- | --- | --- |
| 1A | Casing | 1 |  | 81N | Bearing, Ball, Outboard | 1 |
| 1B | Stuffing Box | 2 |  | 81P | Bearing, Ball, Inboard | 1 |
| 11H | Impeller, 1st Stage | 1 |  | 82N | Housing, Bearing, Inboard | 1 |
| 11J | Impeller, 2nd Stage | 1 |  | 82P | Housing, Bearing, Outboard | 1 |
| 15A | Ring, Casing Wearing | 2 |  | 89N | Locknut, Bearing, Outboard | 1 |
| 16A | Pin, Dowel, Casing Ring | 2 |  | 89P | Locknut, Bearing, Inboard | 1 |
| 16B | Pin, Dowel, Casing Bushing | 1 |  | 91N | Lockwasher, Bearing, Outboard | 1 |
| 18B | Bushing, Casing | 1 |  | 91P | Lockwasher, Bearing, Inboard | 1 |
| 18C | Impeller Spacer | 1 |  | 97N | Bearing Housing Cap | 2 |
| 18D | Stage Piece Bushing | 1 |  | 281A* | Fitting, Zerk | 2 |
| 24A | Key, Impeller | 1 |  | 331A | Packing, Stuffing Box | 1 set |
| 41A | Shaft | 1 |  | 331C | Shaft Sleeve O-Ring | 2 |
| 42A | Sleeve, Shaft | 2 |  | 331D | Stuffing Box O-Ring | 2 |
| 46A | Deflector | 2 |  | 411A | Plug, Pipe, Vent | 2 |
| 71A | Gland, Complete | 2 |  | 411B | Plug, Pipe, Bearing Cap | 1 |
| 72B* | Bolt, Gland, with Nut and Washer | 4 |  | 353A* | Gasket, Casing | 1 |
| 73A | Ring, Lantern | 2 |  | 381B* | Bolt, Casing | Varies |

*Not shown in sectional.

Recommended spare parts are in BOLD.

# Text boxes

PRODUCT BULLETIN			MUNICIPAL				COMMERCIAL			INDUSTRIAL

MODEL HJ MULTISTAGE		Booster Systems, Chemical		HVAC, Booster, Boiler Feed,		Process, Petrochemical,

Injection					High Rise, Condenser Water		Chemical Injection

Bulletin 380HJ

Edition 4e

Bulletin 380HJ

Edition 4e