PRODUCT BULLETIN

MODEL HK MULTISTAGE

Three factors were given top consideration when the American-Marsh Model HK pump was developed by our engineers.  Important operating features combine to give you economical initial cost and installation, plus high, lasting efficiency, with the resultant low operating cost and low maintenance expense because of simplicity of design and ease or replacement parts when necessary – factors that every operating engineer considers most important.

Material Specifications

| PART | CONSTRUCTION |
| --- | --- |
|  | BRONZE FITTED | ALL IRON | NI-RESIST FITTED | 316SS FITTED |
| Casing | Cast Iron | Cast Iron | Cast Iron | Cast Iron |
| Impellers | Bronze | Cast Iron | Ni-Resist | 316 Stainless Steel |
| Shaft | 420 Stainless Steel | 420 Stainless Steel | Stainless | 316 Stainless Steel |
| Lantern Rings | Bronze | Cast Iron | Ni-Resist | 316 Stainless Steel |
| Stuffing Box Glands | Bronze | Cast Iron | Ni-Resist | 316 Stainless Steel |
| Shaft Sleeves | Bronze | 416 Stainless Steel | 316 Stainless Steel | 316 Stainless Steel |
| Bearing Housings | Cast Iron | Cast Iron | Cast Iron | Cast Iron |
| Mechanical Seal | Carbon/Si-C/Buna | Carbon/Si-C/Buna | Carbon/Si-C/Buna | Carbon/Si-C/Buna |

MODEL HK SPECIFICATIONS

Casing:  The casing is of cast iron, or other specified material, of the volute type with external water passages and split on the horizontal centerline with suction and discharge nozzles, cast integral with the lower half.  Removal of the upper half of the casing gives complete access to the interior of the pump without disturbing pipe connections or alignment.  Ample wall thickness provides a generous allowance for corrosion.  The stage arrangement is such that one stuffing box is under suction pressure only with the other box subject only to first stage pressure.  Furthermore, the maximum pressure difference across any of the stage pieces, separating the impeller chambers, is reduced to that of the first stage.  Impellers are opposed or back-to-back to eliminate end thrust and volutes are staggered to balance radial thrust.  This hydraulic balancing of all radial or end thrust is obtained without the use of troublesome balancing disks or other devices that reduce efficiency.  Thus the efficiency of the HK is inherently high and sustained over long periods of time.

Impellers:  The impellers are of bronze or other specified alloy.  They are the single suction, enclosed type, with the outer surfaces machined and polished with hand finished water passages.  Hydraulic balancing is accomplished as described in the above paragraph and impellers are mechanically balanced after machining,

Casing and Impeller Wear Rings:  The case and impeller wear rings are of bronze or other specified material.  Both rings have large wearing surfaces to reduce leakage losses.  Casing wearing rings are held rigidly in the casing by a tongue and groove fit with offset on the horizontal centerline – thus preventing rotation without using holding pins or screws.

Shaft:  The shaft is of 420 stainless steel, or other specified material, ground finished to close tolerances and of ample proportions to safely transmit the maximum power as well as avoiding all critical speeds in operation.  Impeller keys are staggered to prevent uneven stresses and unbalance.

Shaft Sleeves:  The shaft sleeves are of bronze, or other specified material, extending from the impeller hub through the stuffing boxes and secured to the shaft by impeller key extension.  Longitudinal position is maintained by twin locknuts.  Stuffing boxes prevent leakage along the shaft while allowing freedom for the sleeve to expand independently of the shaft expansion.

Stuffing Boxes:  are arranged for water cooling and are extra deep.  Throat bushings protect main casing from wear.  Lantern rings are provided with in-and-out connections provided for both boxes to permit the circulation of sealing water, or a lubricating medium when required by special service conditions.  Stuffing boxes are of the split type for ease in removal when repacking.  A wide variety of mechanical seals are available upon request.

Bearing Housings:  Bearings housings are split on the horizontal centerline, similar to the pump casing, so that the housings need not be detached from the lower part of the casing when removing the rotating element.  The bearings are of the double row type with positive ring-oil lubrication.  The inboard bearing carries the radial load and is free to move in either direction.  The outboard bearing is of the angular contact, duplex type to carry either radial or unbalanced thrust loads and maintain impellers in their proper positions.  The cooling water jacket extends around the entire circumference of the bearing housing so that cooling is uniform and no damaging stresses are set up as might be the case when the cooling jacket is only around one-half the circumference as used in older designs.  No gaskets are required, so cooling water cannot leak into oil reservoirs and bearing replacements will always fit.

HK Sectional Drawing

| Item Number | Item Description | Num. Req. |  | Item Number | Item Description | Num. Req. |
| --- | --- | --- | --- | --- | --- | --- |
| 1A | Casing | 1 |  | 81N | Bearing, Outboard Ball, Thrust | 2 |
| 5A | Stage Piece | 1 |  | 81P | Bearing, Inboard Ball, Radial | 1 |
| 11H | Impeller, First Stage | 1 |  | 82M | Housing, Bearing | 2 |
| 11J | Impeller, Second Stage | 1 |  | 85N | Cap, Outboard Bearing | 1 |
| 13A | Ring, Impeller Wearing, First Stage | 1 |  | 85P | Cap, Inboard Bearing | 1 |
| 13B | Ring, Impeller Wearing, Second Stage | 1 |  | 88D | Ring, Bearing Oil | 2 |
| 15A | Ring, Casing Wearing | 1 |  | 89N | Locknut, Outboard Bearing | 1 |
| 15B | Ring, Casing Wearing | 1 |  | 89P | Locknut, Inboard Bearing | 1 |
| 24A | Key, Impeller, First Stage | 1 |  | 91P | Lockwasher, Inboard Bearing | 2 |
| 41D | Shaft | 1 |  | 92N | Adapter, Outboard Bearing | 1 |
| 42A | Sleeve, Shaft | 2 |  | 108N | Cap, Bearing Manifold, Outboard | 1 |
| 43A | Nut, Shaft Sleeve Lock | 2 |  | 108P | Cap, Bearing Manifold, Inboard | 1 |
| 46A | Slinger, Shaft Fluid, Inbd/Outbd | 1 |  | 109N | Collar, Oil Ring, Outboard | 1 |
| 46B | Slinger, Shaft Fluid, Inbd/Inbd | 1 |  | 109P | Collar, Oil Ring, Inboard | 1 |
| 46C | Slinger, Shaft Fluid, Outbd/Inbd | 1 |  | 181A* | Pipe, Fluid Seal Connecting | 1 set |
| 47A* | Set Screw, Shaft Slinger | 6 |  | 282B* | Oiler, Constant Level | 2 |
| 49A | Gland, Shaft Sleeve | 1 |  | 331A | Packing, Stuffing Box | 1 set |
| 63A | Bushing, Stuffing Box Throat | 2 |  | 331C | O-Ring, Shaft Sleeve | 4 |
| 71A | Gland, Stuffing Box | 2 |  | 353A* | Gasket, Casing | 1 |
| 72C* | Bolt, Gland Hinge | 4 |  | 359A | Gasket, Bearing Housing, Rubber | 2 |
| 73A | Ring, Lantern | 2 |  | 359B | Gasket, Bearing Housing, Manilla | 2 |
| 79B | Gasket, Stuffing Box Gland | 2 |  | 381F* | Nuts, Cap for Casing Studs | Varies |

* Not shown in sectional.

Recommended spare parts are in BOLD.

# Text boxes

PRODUCT BULLETIN			MUNICIPAL				COMMERCIAL			INDUSTRIAL

MODEL HK MULTISTAGE		Booster Systems, Chemical Injection	HVAC, Booster, Boiler Feed,		Process, Petrochemical,

High Rise, Condenser Water		Chemical Injection

Bulletin 380HK

Edition 4c

Bulletin 380HK

Edition 4c